## YJV22
导线标称截面Nominal cross sectional area of conductor (mm2) | 绝缘厚度 Insulation thickness (mm) | 内护套厚度 Inner sheath thickness (mm) | 钢带厚度 Steel tape diameter (mm) | 护套厚度 Sheath thickness (mm) | 电缆近似外径 Approx. overall diameter of cable (mm) | 电缆近似重量Approx weight of cable (kg/m) | 导体直流电阻 D.C resistance of conductor (Ω/km） | 电缆载流量Currentrating
[8 empty] | 在空气中 In air(A) | 直埋土壤里Direct in soil(A)
2*4 | 0.7 | 1.2 | 2*0.3 | 1.8 | 15.7 | 0.433 | ≤4.61 | 34 | 45
2*6 | 0.7 | 1.2 | 2*0.3 | 1.8 | 16.7 | 0.500 | ≤3.08 | 43 | 57
2*10 | 0.7 | 1.4 | 2*0.3 | 1.8 | 19.3 | 0.673 | ≤1.83 | 60 | 77
2*16 | 0.7 | 1.4 | 2*0.3 | 1.8 | 21.4 | 0.857 | ≤1.15 | 83 | 105
2*25 | 0.9 | 1.6 | 2*0.3 | 1.8 | 21.2 | 1.173 | ≤0.727 | 105 | 125
2*35 | 0.9 | 1.6 | 2*0.3 | 1.8 | 23.2 | 1.449 | ≤0.524 | 125 | 155
2*50 | 1.0 | 1.8 | 2*0.3 | 1.8 | 25.0 | 1.877 | ≤0.387 | 160 | 185
2*70 | 1.1 | 1.8 | 2*0.3 | 1.8 | 27.8 | 2.454 | ≤0.268 | 200 | 225
2*95 | 1.1 | 2.0 | 2*0.3 | 1.9 | 30.8 | 2.483 | ≤0.193 | 245 | 270
2*120 | 1.2 | 2.0 | 2*0.3 | 2.0 | 33.4 | 4.213 | ≤0.153 | 285 | 310
2*150 | 1.4 | 2.0 | 2*0.3 | 2.2 | 38.2 | 5.087 | ≤0.124 | 325 | 345
3*1.5 | 0.7 | 1.0 | 2*0.3 | 1.5 | 13 | 0.273 | ≤12.1 | 20 | 27
3*2.5 | 0.7 | 1.0 | 2*0.3 | 1.5 | 14 | 0.321 | ≤7.41 | 26 | 35
3*4 | 0.7 | 1.2 | 2*0.3 | 1.5 | 15 | 0.390 | ≤4.61 | 34 | 45
3*6 | 0.7 | 1.2 | 2*0.3 | 1.5 | 16 | 0.471 | ≤3.08 | 43 | 57
3*10 | 0.7 | 1.4 | 2*0.3 | 1.5 | 18 | 0.622 | ≤1.83 | 60 | 77
3*16 | 0.7 | 1.4 | 2*0.5 | 2.0 | 22 | 1.005 | ≤1.15 | 83 | 105
3*25 | 0.9 | 1.6 | 2*0.5 | 2.0 | 25 | 1.371 | ≤0.727 | 105 | 125
3*35 | 0.9 | 1.6 | 2*0.5 | 2.0 | 27 | 1.724 | ≤0.524 | 125 | 155
3*50 | 1.0 | 1.8 | 2*0.5 | 2.0 | 30 | 2.247 | ≤0.387 | 160 | 185
3*70 | 1.1 | 1.8 | 2*0.5 | 2.5 | 35 | 3.023 | ≤0.268 | 200 | 225
3*95 | 1.1 | 2.0 | 2*0.5 | 2.5 | 39 | 3.825 | ≤0.193 | 245 | 270
3*120 | 1.2 | 2.0 | 2*0.5 | 2.5 | 42 | 4.642 | ≤0.153 | 285 | 310
3*150 | 1.4 | 2.0 | 2*0.5 | 3.0 | 48 | 5.767 | ≤0.124 | 325 | 345
3*185 | 1.6 | 2.2 | 2*0.5 | 3.0 | 51 | 6.895 | ≤0.0991 | 375 | 390
3*240 | 1.7 | 2.2 | 2*0.5 | 3.0 | 56 | 8.617 | ≤0.0754 | 440 | 450
3*300 | 1.8 | 2.2 | 2*0.5 | 3.0 | 59 | 10.928 | ≤0.0601 | 505 | 515
3*400 | 2.0 | 2.2 | 2*0.5 | 3.2 | 61 | 13.556 | ≤0.0470 | 570 | 575
4*4 | 0.7 | 1.0 | 2*0.3 | 1.5 | 16 | 0.454 | ≤4.61 | 34 | 45
4*6 | 0.7 | 1.0 | 2*0.3 | 1.5 | 17 | 0.557 | ≤3.08 | 43 | 57
4*10 | 0.7 | 1.0 | 2*0.3 | 2.0 | 20 | 0.791 | ≤1.83 | 60 | 77
4*16 | 0.7 | 1.0 | 2*0.5 | 2.0 | 23 | 1.210 | ≤1.15 | 83 | 105
4*25 | 0.9 | 1.0 | 2*0.5 | 2.0 | 27 | 1.672 | ≤0.727 | 105 | 125
4*35 | 0.9 | 1.0 | 2*0.5 | 2.0 | 29 | 2.127 | ≤0.524 | 125 | 155
4*50 | 1.0 | 1.0 | 2*0.5 | 2.0 | 33 | 2.802 | ≤0.387 | 160 | 185
4*70 | 1.1 | 1.2 | 2*0.5 | 2.5 | 38 | 3.785 | ≤0.268 | 200 | 225
4*95 | 1.1 | 1.2 | 2*0.5 | 2.5 | 42 | 4.829 | ≤0.193 | 245 | 270
4*120 | 1.2 | 1.4 | 2*0.5 | 3.0 | 47 | 6.033 | ≤0.153 | 285 | 310
4*150 | 1.4 | 1.4 | 2*0.5 | 3.0 | 52 | 7.356 | ≤0.124 | 325 | 345
4*185 | 1.6 | 1.6 | 2*0.5 | 3.0 | 56 | 8.808 | ≤0.0991 | 375 | 390
4*240 | 1.7 | 1.6 | 2*0.5 | 3.0 | 62 | 11.182 | ≤0.0754 | 440 | 450
4*300 | 1.8 | 1.7 | 2*0.5 | 3.1 | 64 | 14.176 | ≤0.0601 | 505 | 515
4*400 | 2.0 | 1.7 | 2*0.5 | 3.5 | 69 | 17.815 | ≤0.0470 | 570 | 575
5*4 | 0.7 | 1.0 | 2*0.3 | 1.5 | 16 | 0.588 | ≤4.61 | 34 | 45
5*6 | 0.7 | 1.0 | 2*0.3 | 1.5 | 17 | 0.720 | ≤3.08 | 43 | 57
5*10 | 0.7 | 1.0 | 2*0.3 | 2.0 | 20 | 1.014 | ≤1.83 | 60 | 77
5*16 | 0.7 | 1.0 | 2*0.5 | 2.0 | 23 | 1.392 | ≤1.15 | 83 | 105
5*25 | 0.9 | 1.0 | 2*0.5 | 2.0 | 26 | 2.002 | ≤0.727 | 105 | 125
5*35 | 0.9 | 1.0 | 2*0.5 | 2.0 | 28 | 2.581 | ≤0.524 | 125 | 155
5*50 | 1.0 | 1.0 | 2*0.5 | 2.0 | 31 | 3.722 | ≤0.387 | 160 | 185
5*70 | 1.1 | 1.2 | 2*0.5 | 2.5 | 36 | 4.897 | ≤0.268 | 200 | 225
5*95 | 1.1 | 1.2 | 2*0.5 | 2.5 | 40 | 6.338 | ≤0.193 | 245 | 270
5*120 | 1.2 | 1.4 | 2*0.5 | 3.0 | 44 | 7.851 | ≤0.153 | 285 | 310
5*150 | 1.4 | 1.4 | 2*0.5 | 3.0 | 49 | 9.661 | ≤0.124 | 325 | 345
5*185 | 1.6 | 1.6 | 2*0.5 | 3.0 | 52 | 11.770 | ≤0.0991 | 375 | 390
5*240 | 1.7 | 1.6 | 2*0.5 | 3.0 | 68 | 14.900 | ≤0.0754 | 440 | 450
5*300 | 1.8 | 1.7 | 2*0.5 | 3.1 | 71 | 18.000 | ≤0.0601 | 505 | 515
3*4+1*2.5 | 0.7 | 1.0 | 2*0.3 | 1.5 | 16 | 0.443 | ≤4.61 | 34 | 45
3*6+1*4 | 0.7 | 1.0 | 2*0.3 | 1.5 | 17 | 0.531 | ≤3.08 | 43 | 57
3*10+1*6 | 0.7 | 1.0 | 2*0.3 | 2.0 | 20 | 0.741 | ≤1.83 | 60 | 77
3*16+1*10 | 0.7 | 1.0 | 2*0.5 | 2.0 | 23 | 1.135 | ≤1.15 | 83 | 105
3*25+1*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 26 | 1.556 | ≤0.727 | 105 | 125
3*35+1*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 28 | 1.896 | ≤0.524 | 125 | 155
3*50+1*25 | 1.0 | 1.0 | 2*0.5 | 2.0 | 31 | 2.518 | ≤0.387 | 160 | 185
3*70+1*35 | 1.1 | 1.2 | 2*0.5 | 2.5 | 36 | 3.293 | ≤0.268 | 200 | 225
3*95+1*50 | 1.1 | 1.2 | 2*0.5 | 2.5 | 40 | 4.349 | ≤0.193 | 245 | 270
3*120+1*70 | 1.2 | 1.2 | 2*0.5 | 2.5 | 44 | 5.365 | ≤0.153 | 285 | 310
3*150+1*70 | 1.4 | 1.4 | 2*0.5 | 3.0 | 49 | 6.468 | ≤0.124 | 325 | 345
3*185+1*95 | 1.6 | 1.4 | 2*0.5 | 3.0 | 52 | 7.854 | ≤0.0991 | 375 | 390
3*240+1*120 | 1.7 | 1.6 | 2*0.5 | 3.5 | 68 | 9.814 | ≤0.0754 | 440 | 450
3*300+1*150 | 1.8 | 1.7 | 2*0.5 | 3.5 | 71 | 12.781 | ≤0.0601 | 505 | 515
4*4+1*2.5 | 0.7 | 1.0 | 2*0.3 | 1.5 | 18.4 | 0.565 | ≤4.61 | 34 | 45
4*6+1*4 | 0.7 | 1.0 | 2*0.3 | 1.5 | 19.8 | 0.692 | ≤3.08 | 43 | 57
4*10+1*6 | 0.7 | 1.0 | 2*0.3 | 2.0 | 22.8 | 0.953 | ≤1.83 | 60 | 77
4*16+1*10 | 0.7 | 1.0 | 2*0.5 | 2.0 | 25.8 | 1.318 | ≤1.15 | 83 | 105
4*25+1*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 30.4 | 1.877 | ≤0.727 | 105 | 125
4*35+1*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 34.1 | 2.324 | ≤0.524 | 125 | 155
4*50+1*25 | 1.0 | 1.0 | 2*0.5 | 2.0 | 38.7 | 3.415 | ≤0.387 | 160 | 185
4*70+1*35 | 1.1 | 1.2 | 2*0.5 | 2.5 | 44.2 | 4.432 | ≤0.268 | 200 | 225
4*95+1*50 | 1.1 | 1.2 | 2*0.5 | 2.5 | 49.8 | 5.747 | ≤0.193 | 245 | 270
4*120+1*70 | 1.2 | 1.2 | 2*0.5 | 2.5 | 55.4 | 7.112 | ≤0.153 | 285 | 310
4*150+1*70 | 1.4 | 1.4 | 2*0.5 | 3.0 | 60.1 | 8.556 | ≤0.124 | 325 | 345
4*185+1*95 | 1.6 | 1.4 | 2*0.5 | 3.0 | 66.9 | 10.510 | ≤0.0991 | 375 | 390
4*240+1*120 | 1.7 | 1.6 | 2*0.5 | 3.5 | 74.8 | 13.232 | ≤0.0754 | 440 | 450
4*300+1*150 | 1.8 | 1.7 | 2*0.5 | 3.5 | 78.4 | 16.452 | ≤0.0601 | 505 | 515
3*4+2*2.5 | 0.7 | 1.0 | 2*0.3 | 1.5 | 17.5 | 0.855 | ≤4.61 | 34 | 45
3*6+2*4 | 0.7 | 1.0 | 2*0.3 | 1.5 | 18.9 | 1.009 | ≤3.08 | 43 | 57
3*10+2*6 | 0.7 | 1.0 | 2*0.3 | 2.0 | 21.6 | 1.461 | ≤1.83 | 60 | 77
3*16+2*10 | 0.7 | 1.0 | 2*0.5 | 2.0 | 24.6 | 1.877 | ≤1.15 | 83 | 105
3*25+2*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 28.7 | 2.583 | ≤0.727 | 105 | 125
3*35+2*16 | 0.9 | 1.0 | 2*0.5 | 2.0 | 30.7 | 3.001 | ≤0.524 | 125 | 155
3*50+2*25 | 1.0 | 1.0 | 2*0.5 | 2.0 | 36.2 | 4.392 | ≤0.387 | 160 | 185
3*70+2*35 | 1.1 | 1.2 | 2*0.5 | 2.5 | 40.3 | 5.519 | ≤0.268 | 200 | 225
3*95+2*50 | 1.1 | 1.2 | 2*0.5 | 2.5 | 44.9 | 7.543 | ≤0.193 | 245 | 270
3*120+2*70 | 1.2 | 1.2 | 2*0.5 | 2.5 | 50.3 | 9.203 | ≤0.153 | 285 | 310
3*150+2*70 | 1.4 | 1.4 | 2*0.5 | 3.0 | 54.0 | 10.485 | ≤0.124 | 325 | 345
3*185+2*95 | 1.6 | 1.4 | 2*0.5 | 3.0 | 60.2 | 13.945 | ≤0.0991 | 375 | 390
3*240+2*120 | 1.7 | 1.6 | 2*0.5 | 3.5 | 67.2 | 15.643 | ≤0.0754 | 440 | 450
3*300+2*150 | 1.8 | 1.7 | 2*0.5 | 3.5 | 75.2 | 18.204 | ≤0.0601 | 505 | 515